## AF-Calc
Arc Flash Calculator for Arcing Current and Incident Energy - to IEEE 1584 - 2002
Note: Only one contribution to bus arcing fault.
|  |  | Un < 1kV |  | 0.85 x Ia | Un=>1kV |  | Un>15kV
Lee Method
Input data |  | J / cal = | 4.184
Nom Voltage |  | V(kV) | 0.415 |  | 0.415 | 1 |  | 33 | Nominal Voltage
Fault Current |  | Ibf(kA) | 19.931 |  | 19.931 | 19.931 |  | 8.06 | Bolted three phase short-circuit current
Working Dist |  | D (mm) | 457 |  | 457 | 457 |  | 910 | Working distance between arc and worker's chest and face
AS 4836 = 500mm for 415V
Fault Clearing Time |  | t(s) | 0.03 |  | 3.358 | 0.03 |  | 0.978 | Relay tripping time plus breaker clearing time
Bus bar Gap - MCC/Pnl |  | G = 25mm | 25 |  | 25 | 25 |  |  | Distance between conductive parts
Bus bar Gap - SwGr |  | G = 32mm | [6 empty] | IEEE 1584 Table 2
Arc in box |  | K = -0.097 | -0.097 |  | -0.097 | -0.097 |  |  | see IEEE 1584 section 5.2 equation 1
Arc in open |  | K = -0.153
|  | log(Ia) | 1.0191 |  | 0.94855 | 1.2815 |  |  | Log ( arcing current )
Arc Current |  | Ia | 10.4502 | 0.85 | 8.8827 | 19.1186 |  |  | Arcing current
Arc in box |  | K1 = -0.555 | -0.555 |  | -0.555 | -0.555 |  |  | see IEEE 1584 section 5.3 equation 4
Arc in open |  | K1 = -0.792
Grounded system |  | K2 = -0.113 | 0 |  | 0 | 0 |  |  | see IEEE 1584 section 5.3 equation 4
Ungrounded system |  | K2 = 0
|  | log(En) | 0.57418 |  | 0.49788 | 0.85776 |  |  | Log ( Incident energy normalized for arcing time of 0.2 sec and
working distance of 610 mm )
|  | En | 3.7512 |  | 3.1469 | 7.207 |  |  | Incident energy normalized for arcing time of 0.2 sec and
working distance of 610 mm )
Panel/MCC Distance Factor |  | x = 1.641 | 1.641 |  | 1.641 | 1.641 |  |  | See table 4 of IEEE 1584
SwGr Distance Factor |  | x = 1.473
Un =< 1000V |  | Cf = 1.5 | 1.5 |  | 1.5 | 1.5 |  |  | See equi 6 of IEEE 1584
Un > 1000V |  | Cf = 1.0
IEEE - Inc Energy (J/cm2) |  | IEEE 1584 | 5.6722 |  | 532.6169 | 10.8977 |  |  | Incident Energy
IEEE - Inc Energy (cal/cm2) |  | IEEE 1584 | 1.3557 |  | 127.2985 | 2.6046 |  |  | Incident Energy
Lee Method - (J/cm²) |  | Lee Method | [5 empty] | 672.8597 | Incident Energy
Lee Method - (cal/cm²) |  | Lee Method | [5 empty] | 160.8173 | Incident Energy
Arc Flash Boundary ( DB ) |  | mm | 492.2683 |  | 7839.9104 | 732.8427 |  | 10556.4683
5.0208 | Cal/cm^2
1.2 | J/cm^2