SKM’s  PTW Arc Flash IEEE 1584-2018 calculates additional:

- “Flash Boundaries” based on user defined incident energy, and

- “Incident Energy” based on user defined additional Working Distances.

My manual calculations agree with the PTW32 Ver 9003 results  2), 3), and 4) in Fig. 1 below.

However the PTW  results 11) and 12) in Fig. 1 below are incorrect.

Figure 1 - SKM PTW IEEE1584-2018 Results

Can someone validate my calculations which show:

-	11)  AF_FB@IE1 = 2524 mm, at 1.2 Cal/cm2

-	12)  AF_FB@IE2 = 610 mm, at 11.62 Cal/cm2

Can someone validate my calculations for 11) and 12) using a IEEE 1584-2018  spreadsheet ?

The correct results for 2), 3), 4) contradict the  incorrect results  for 11) and 12).