For Iarc graph (yellow background) 430V, 32mm gap (1.25 inches), 415V, 36mm gap. Note Iarc is lower for lower V/larger gap conservative.

Using the above Iarc variables, with 18” working distance and 100ms protection EI is about the same, which means that using the lower V and adding a bit to the gaps would yield a single, conservative calculation.  Ended up ~ 13% larger gap to get this particular result.

Keep in mind that if protection is “inverse” at higher current the protection is faster so AF results would be better than what the graph below indicates, which applies if protection is definite (fixed) time!

Calculations done using HCB, Std LV box.

Point being AF calculations are not exact, but if biased so the error is acceptable then they are useful.

Marcelo.e.valdes@ieee.org